## perimeter
Measure the perimeter of the blocks, have the sum of it
SUM of the perimeter on the map | 362.3 | cm
| 3.623 | m | 1
| 18115 | m | 5000
Divide by 25
Count of connections | 724.6
what is yellow | is given on your worksheet or calculated on the previous page

## water demand
DOMESTIC WATER DEMAND
Count of connections | Persons per connection | Persons | Secific water demand | Average water demand | Seasonal ratio | Peak water demand | Loss coefficient | Designing peak water demand
piece | person/binding in | head | l/person/day | m3/day | - | m3/day | - | m3/day
725 | 3.2 | 2320 | 120 | 278.4 | 1.5 | 417.6 | 1.1 | 459.36
PUBLIC INSTITUTIONS WATER DEMAND
Profession of people | Number of people | specific water demand | average water demand | seasonal ratio | peak water demand | loss coefficient | designing peak water demand
|  | l/person/day | m3/day | - | m3/day | - | m3/day
worker | 60 | 120 | 7.2 | 1.5 | 10.8 | 1.1 | 11.88
student | 800 | 120 | 96 | 1.5 | 144 | 1.1 | 158.4
SUM | [6 empty] | 170.28
THE INDUSTRIAL WATER DEMAND
Technological water demand | loss coefficient | designing peak water demand
m3/day | - | m3/day
1600 | 1.1 | 1760
Number of people | specific water demand | average water demand | seasonal ratio | peak water demand | loss coefficient | designing peak water demand
| l/person/day | m3/day | - | m3/day | - | m3/day
250 | 130 | 32.5 | 1.5 | 48.75 | 1.1 | 53.625
Note on C5: Measure and summarize the perimeter of the blocks and divide by 25 (meter!) Scale: 1:5000

## cons. of nodes
Branches | Length | Q branches | Q node 1 | Q node 2 | Node | Branch (m3/day) | [10 empty] | Node |  |  | Q dweller | Q public ins. | Q ind. soc. | Q people | Q ind. tech. | Q fire
| m | m3/day | m3/day | m3/day | m3/day | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10-11 | 11-2 | m3/day |  | Node | m3/day | m3/day | m3/day | m3/day | m3/day | l/min
1-2 | 90 | 25.7746 | 12.8873 | 12.8873 | 1 | Branch (m3/day) 1-2: 12.8873 | 12.8873 |  | 1 | 12.8873 |  |  | 12.8873
2-3 | 205 | 58.7087 | 29.3544 | 29.3544 | 2 | Branch (m3/day) 1-2: 12.8873; Branch (m3/day) 2-3: 29.3544; Branch (m3/day) 11-2: 27.9224 | 70.1641 |  | 2 | 70.1641 |  |  | 70.1641
3-4 | 115 | 32.9342 | 16.4671 | 16.4671 | 3 | Branch (m3/day) 2-3: 29.3544; Branch (m3/day) 3-4: 16.4671 | 45.8214 |  | 3 | 45.8214 |  |  | 45.8214
4-5 | 173 | 49.5444 | 24.7722 | 24.7722 | 4 | Branch (m3/day) 3-4: 16.4671; Branch (m3/day) 4-5: 24.7722 | 41.2393 |  | 4 | 41.2393 |  |  | 41.2393
5-6 | 158 | 45.2487 | 22.6243 | 22.6243 | 5 | Branch (m3/day) 4-5: 24.7722; Branch (m3/day) 5-6: 22.6243 | 47.3966 |  | 5 | 47.3966 |  |  | 47.3966
6-7 | 110 | 31.5022 | 15.7511 | 15.7511 | 6 | Branch (m3/day) 5-6: 22.6243; Branch (m3/day) 6-7: 15.7511 | 38.3755 | SCHOOL | 6 | 38.3755 | 170.28 |  | 208.6555
7-8 | 128 | 36.6572 | 18.3286 | 18.3286 | 7 | Branch (m3/day) 6-7: 15.7511; Branch (m3/day) 7-8: 18.3286 | 34.0797 |  | 7 | 34.0797 |  |  | 34.0797
8-9 | 135 | 38.6618 | 19.3309 | 19.3309 | 8 | Branch (m3/day) 7-8: 18.3286; Branch (m3/day) 8-9: 19.3309 | 37.6595 | INDUSTRY | 8 | 37.6595 |  | 53.625 | 91.2845 | 1760
9-10 | 155 | 44.3895 | 22.1948 | 22.1948 | 9 | Branch (m3/day) 8-9: 19.3309; Branch (m3/day) 9-10: 22.1948 | 41.5257 |  | 9 | 41.5257 |  |  | 41.5257
10-11 | 140 | 40.0938 | 20.0469 | 20.0469 | 10 | Branch (m3/day) 9-10: 22.1948; Branch (m3/day) 10-11: 20.0469 | 42.2416 | FIRE | 10 | 42.2416 |  |  | 42.2416 |  | 900
11-2 | 195 | 55.8449 | 27.9224 | 27.9224 | 11 | Branch (m3/day) 10-11: 20.0469; Branch (m3/day) 11-2: 27.9224 | 47.9693 |  | 11 | 47.9693 |  |  | 47.9693
SUM | 1604 | 459.36 | [16 empty] | SUM | 459.36 | 170.28 | 53.625 | 683.265 | 1760 | 900
2443.265
Note on D1: Measure the length of the branches (meter!), from your map, after drawing the main loop
Note on E1: Distribute the consumption to the branches in the proportion of the length of the branches
Note on W8: After drawing the main loop decide which nodes should have the school, industry and firefighting water
Note on E14: Designing DOMESTIC peak water demand

## max-min-avg
|  |  |  | minimum consumption (1 %) |  |  |  | average consumption
| Q people | Q ind tech | Q fire | Q people | Q ind. tech | Q fire | Q node | divide Q (m3/day) by 24 -> m3/hour
Node | m3/day | m3/day | l/min | l/s |  |  |  | multiply by 1000 (m3 -> l)
1 | 12.8873 |  |  | 0.035798 |  | - | 0.035798 | divide by 3600 (hour -> s)
2 | 70.1641 |  |  | 0.1949 |  | - | 0.1949
3 | 45.8214 |  |  | 0.12728 |  | - | 0.12728 | 1/24= | 0.041667
4 | 41.2393 |  |  | 0.11455 |  | - | 0.11455
5 | 47.3966 |  |  | 0.13166 |  | - | 0.13166 | minimum consumption
6 | 208.6555 |  |  | 0.5796 |  | - | 0.5796 | mutiply by | 0.01 | -> m3/hour
7 | 34.0797 |  |  | 0.094666 |  | - | 0.094666 | change the units to l/s
8 | 91.2845 | 1760 |  | 0.25357 | 20.3704 | - | 20.6239 | no firefighting water
9 | 41.5257 |  |  | 0.11535 |  | - | 0.11535 | technological water is average
10 | 42.2416 |  | 900 | 0.11734 |  | - | 0.11734
11 | 47.9693 |  |  | 0.13325 |  | - | 0.13325 | maximum consumption
Q cons | 683.265 | 1760 | 900 | 1.898 | 20.3704 | - | 22.2683 | mutiply by | 0.08 | ->m3/hour
change the units to l/s
no firefighting water
|  |  |  | maximum consumption (8 %) |  |  |  | technological water is average
| Q people | Q ind tech | Q fire | Q people | Q ind. tech | Q fire | Q node
Node | m3/day | m3/day | l/min | l/s
1 | 12.8873 |  |  | 0.28638 |  | - | 0.28638
2 | 70.1641 |  |  | 1.5592 |  | - | 1.5592
3 | 45.8214 |  |  | 1.0183 |  | - | 1.0183
4 | 41.2393 |  |  | 0.91643 |  | - | 0.91643
5 | 47.3966 |  |  | 1.0533 |  | - | 1.0533
6 | 208.6555 |  |  | 4.6368 |  | - | 4.6368
7 | 34.0797 |  |  | 0.75733 |  | - | 0.75733
8 | 91.2845 | 1760 |  | 2.0285 | 20.3704 | - | 22.3989
9 | 41.5257 |  |  | 0.92279 |  | - | 0.92279
10 | 42.2416 |  | 900 | 0.9387 |  | - | 0.9387
11 | 47.9693 |  |  | 1.066 |  | - | 1.066
Q cons | 683.265 | 1760 | 900 | 15.1837 | 20.3704 | - | 35.554
average consumption (4.17 %) + fire
| Q people | Q ind tech | Q fire | Q people | Q ind. tech | Q fire | Q node
Node | m3/day | m3/day | l/min | l/s
1 | 12.8873 |  |  | 0.14916 |  |  | 0.14916
2 | 70.1641 |  |  | 0.81208 |  |  | 0.81208
3 | 45.8214 |  |  | 0.53034 |  |  | 0.53034
4 | 41.2393 |  |  | 0.47731 |  |  | 0.47731
5 | 47.3966 |  |  | 0.54857 |  |  | 0.54857
6 | 208.6555 |  |  | 2.415 |  |  | 2.415
7 | 34.0797 |  |  | 0.39444 |  |  | 0.39444
8 | 91.2845 | 1760 |  | 1.0565 | 20.3704 |  | 21.4269
9 | 41.5257 |  |  | 0.48062 |  |  | 0.48062
10 | 42.2416 |  | 900 | 0.48891 |  | 15 | 15.4889
11 | 47.9693 |  |  | 0.5552 |  |  | 0.5552
Q cons | 683.265 | 1760 | 900 | 7.9082 | 20.3704 | 15 | 43.2785
Note on D2: Q dweller + Q inst (students+teachers) + Q ind social
Note on H2: average! x/24 or *0,0417

## initial flow
maximum consumption | [5 empty] | Kirchoff's 1st law (node balance)
Branch | Qin (l/s) | Node | Qnode (l/s) | Branches | Qbranch (l/s) | ƩQi=0
| 35.554 | 1 | 0.28638 | 1-2 | 35.2677
1-2 | 35.2677 | 2 | 1.5592 | 2-3 | 16.8542 | node 1 |  | node 2
2-3 | 16.8542 | 3 | 1.0183 | 3-4 | 15.836 | 35.554 | 35.2677 | 35.2677 | 16.8542 | 50%
3-4 | 15.836 | 4 | 0.91643 | 4-5 | 14.9195
4-5 | 14.9195 | 5 | 1.0533 | 5-6 | 13.8663
5-6 | 13.8663 | 6 | 4.6368 | 6-7 | 9.2295 |  | 0.28638 | 16.8542 |  | 1.5592
6-7 | 9.2295 | 7 | 0.75733 | 7-8 | 8.4722 |  |  | 50%
7-8 | 8.4722 | 8 | 22.3989 | 8-9 | -13.9267
8-9 | -13.9267 | 9 | 0.92279 | 9-10 | -14.8495
9-10 | -14.8495 | 10 | 0.9387 | 10-11 | -15.7882 | node 3 |  | node 11
10-11 | -15.7882 | 11 | 1.066 | 11-2 | -16.8542 | 16.8542 | 15.836 | -15.7882 | -16.8542
11-2 | -16.8542
[7 empty] | 1.0183 |  | 1.066
minimum consumption
Branch | Qin (l/s) | Node | Qnode (l/s) | Branches | Qbranch (l/s)
| 22.2683 | 1 | 0.035798 | 1-2 | 22.2325
1-2 | 22.2325 | 2 | 0.1949 | 2-3 | 11.0188
2-3 | 11.0188 | 3 | 0.12728 | 3-4 | 10.8915
3-4 | 10.8915 | 4 | 0.11455 | 4-5 | 10.777
4-5 | 10.777 | 5 | 0.13166 | 5-6 | 10.6453
5-6 | 10.6453 | 6 | 0.5796 | 6-7 | 10.0657
6-7 | 10.0657 | 7 | 0.094666 | 7-8 | 9.9711
7-8 | 9.9711 | 8 | 20.6239 | 8-9 | -10.6529
8-9 | -10.6529 | 9 | 0.11535 | 9-10 | -10.7682
9-10 | -10.7682 | 10 | 0.11734 | 10-11 | -10.8856
10-11 | -10.8856 | 11 | 0.13325 | 11-2 | -11.0188
11-2 | -11.0188
average consumption
Branch | Qin (l/s) | Node | Qnode (l/s) | Branches | Qbranch (l/s)
| 43.2785 | 1 | 0.14916 | 1-2 | 43.1294
1-2 | 43.1294 | 2 | 0.81208 | 2-3 | 21.1586
2-3 | 21.1586 | 3 | 0.53034 | 3-4 | 20.6283
3-4 | 20.6283 | 4 | 0.47731 | 4-5 | 20.151
4-5 | 20.151 | 5 | 0.54857 | 5-6 | 19.6024
5-6 | 19.6024 | 6 | 2.415 | 6-7 | 17.1874
6-7 | 17.1874 | 7 | 0.39444 | 7-8 | 16.793
7-8 | 16.793 | 8 | 21.4269 | 8-9 | -4.6339
8-9 | -4.6339 | 9 | 0.48062 | 9-10 | -5.1145
9-10 | -5.1145 | 10 | 15.4889 | 10-11 | -20.6034
10-11 | -20.6034 | 11 | 0.5552 | 11-2 | -21.1586
11-2 | -21.1586
Note on F2: MAX Q node
Note on D3: MAX consumption
Note on H4: assumption: 50-50% to branch 2-3 and branch 11-2
Note on F21: MIN Q node
Note on D22: MIN consumption
Note on H23: assumption: 50-50% to branch 2-3 and branch 11-2
Note on F37: AVG Q node
Note on D38: AVG consumption
Note on H39: assumption: 50-50% to branch 2-3 and branch 11-2

## diameter calc
Branch | Qbranch (l/s) | Qbranch (m3/s) | Calculated diameter (m) | Diameter (mm)
1-2 | 35.2677 | 0.035268 | 0.21191 | 200
2-3 | 16.8542 | 0.016854 | 0.14649 | 150
3-4 | 15.836 | 0.015836 | 0.142 | 150
4-5 | 14.9195 | 0.01492 | 0.13783 | 150
5-6 | 13.8663 | 0.013866 | 0.13287 | 150
6-7 | 9.2295 | 0.0092295 | 0.1084 | 150
7-8 | 8.4722 | 0.0084722 | 0.10386 | 150
8-9 | -13.9267 | -0.013927 | 0.13316 | 150
9-10 | -14.8495 | -0.01485 | 0.1375 | 150
10-11 | -15.7882 | -0.015788 | 0.14178 | 150
11-2 | -16.8542 | -0.016854 | 0.14649 | 150

## Cross
MAXIMUM CONSUMPTION | [5 empty] | 1. iteration | [5 empty] | 2. iteration
Branch | Lenght (m) | Diameter (mm) | main-ring | Sign | C [s2/m5] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ
1-2 | 90 | 200 | branch | 1 | 766.8805 | 0.035268 | 54.0922 | 0.95385 |  |  |  | 0.035268 | 0.035268
2-3 | 205 | 150 |  | 1 | 7360.9309 | 0.016854 | 248.1256 | 2.091 | 248.1256 | 2.091 |  | 0.016308 | 0.016308 | 240.0771 | 1.9575 | 240.0771 | 1.9575
3-4 | 115 | 150 |  | 1 | 4129.3027 | 0.015836 | 130.783 | 1.0355 | 378.9086 | 3.1265 |  | 0.015289 | 0.015289 | 126.268 | 0.96527 | 366.3451 | 2.9228
4-5 | 173 | 150 |  | 1 | 6211.9075 | 0.01492 | 185.3576 | 1.3827 | 564.2662 | 4.5092 |  | 0.014373 | 0.014373 | 178.5655 | 1.2832 | 544.9106 | 4.2061
5-6 | 158 | 150 |  | 1 | 5673.3028 | 0.013866 | 157.3353 | 1.0908 | 721.6015 | 5.6001 |  | 0.01332 | 0.01332 | 151.132 | 1.0065 | 696.0426 | 5.2126
6-7 | 110 | 150 | one-loop | 1 | 3949.7678 | 0.0092295 | 72.9087 | 0.33646 | 794.5103 | 5.9365 |  | 0.0086828 | 0.0086828 | 68.59 | 0.29778 | 764.6326 | 5.5103
7-8 | 128 | 150 |  | 1 | 4596.0934 | 0.0084722 | 77.8778 | 0.3299 | 872.388 | 6.2664 |  | 0.0079255 | 0.0079255 | 72.8524 | 0.28869 | 837.485 | 5.799
8-9 | 135 | 150 |  | 1 | 4847.4423 | -0.013927 | 135.0182 | -0.94018 | 1007.4062 | 5.3262 |  | -0.014473 | -0.014473 | 140.3184 | -1.0154 | 977.8034 | 4.7836
9-10 | 155 | 150 |  | 1 | 5565.5819 | -0.01485 | 165.2926 | -1.2273 | 1172.6988 | 4.099 |  | -0.015396 | -0.015396 | 171.3781 | -1.3193 | 1149.1815 | 3.4643
10-11 | 140 | 150 |  | 1 | 5026.9772 | -0.015788 | 158.7342 | -1.2531 | 1331.4331 | 2.8459 |  | -0.016335 | -0.016335 | 164.2308 | -1.3414 | 1313.4123 | 2.1229
11-2 | 195 | 150 |  | 1 | 7001.8611 | -0.016854 | 236.0219 | -1.989 | 1567.455 | 0.85693 | -0.0005467 | -0.017401 | -0.017401 | 243.6778 | -2.1201 | 1557.0901 | 0.0028333 | -1.8196e-06
[10 empty] | failure | [6 empty] | failure
MINIMUM CONSUMPTION | [5 empty] | 1. iteration | [5 empty] | 2. iteration
Branch | Lenght (m) | Diameter (mm) | main-ring | Sign | C [s2/m5] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ
1-2 | 90 | 200 | branch | 1 | 766.8805 | 0.022233 | 34.0994 | 0.37906 |  |  |  | 0.022233 | 0.022233
2-3 | 205 | 150 |  | 1 | 7360.9309 | 0.011019 | 162.2175 | 0.89372 | 162.2175 | 0.89372 |  | 0.010191 | 0.010191 | 150.0368 | 0.76454 | 150.0368 | 0.76454
3-4 | 115 | 150 |  | 1 | 4129.3027 | 0.010892 | 89.9489 | 0.48984 | 252.1664 | 1.3836 |  | 0.010064 | 0.010064 | 83.1158 | 0.41825 | 233.1527 | 1.1828
4-5 | 173 | 150 |  | 1 | 6211.9075 | 0.010777 | 133.8912 | 0.72147 | 386.0576 | 2.105 |  | 0.0099496 | 0.0099496 | 123.6119 | 0.61494 | 356.7646 | 1.7977
5-6 | 158 | 150 |  | 1 | 5673.3028 | 0.010645 | 120.7883 | 0.64292 | 506.8458 | 2.7479 |  | 0.0098179 | 0.0098179 | 111.4003 | 0.54686 | 468.1648 | 2.3446
6-7 | 110 | 150 | one-loop | 1 | 3949.7678 | 0.010066 | 79.5145 | 0.40019 | 586.3604 | 3.1481 |  | 0.0092383 | 0.0092383 | 72.9786 | 0.3371 | 541.1434 | 2.6817
7-8 | 128 | 150 |  | 1 | 4596.0934 | 0.0099711 | 91.6558 | 0.45695 | 678.0162 | 3.6051 |  | 0.0091437 | 0.0091437 | 84.0504 | 0.38426 | 625.1938 | 3.066
8-9 | 135 | 150 |  | 1 | 4847.4423 | -0.010653 | 103.2784 | -0.55011 | 781.2947 | 3.055 |  | -0.01148 | -0.01148 | 111.2998 | -0.63888 | 736.4936 | 2.4271
9-10 | 155 | 150 |  | 1 | 5565.5819 | -0.010768 | 119.8629 | -0.64536 | 901.1576 | 2.4096 |  | -0.011596 | -0.011596 | 129.0727 | -0.74834 | 865.5663 | 1.6787
10-11 | 140 | 150 |  | 1 | 5026.9772 | -0.010886 | 109.443 | -0.59567 | 1010.6006 | 1.814 |  | -0.011713 | -0.011713 | 117.7615 | -0.68967 | 983.3278 | 0.98908
11-2 | 195 | 150 |  | 1 | 7001.8611 | -0.011019 | 154.3044 | -0.85013 | 1164.905 | 0.96383 | -0.00082739 | -0.011846 | -0.011846 | 165.8909 | -0.98259 | 1149.2187 | 0.0064893 | -5.6467e-06
[10 empty] | failure | [6 empty] | failure
AVERAGE CONSUMPTION | [5 empty] | 1. iteration | [5 empty] | 2. iteration | [6 empty] | 3. iteration
Branch | Lenght (m) | Diameter (mm) | main-ring | Sign | C [s2/m5] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ | Q[m3/s] | Q[m3/s] | 2abs(CQ) | C*Q*abs(Q) | Σ2abs(CQ) | ΣC*Q*abs(Q) | ΔQ
1-2 | 90 | 200 | branch | 1 | 766.8805 | 0.043129 | 66.1501 | 1.4265 |  |  |  | 0.043129 | 0.043129 | [5 empty] | 0.043129 | 0.043129
2-3 | 205 | 150 |  | 1 | 7360.9309 | 0.021159 | 311.4946 | 3.2954 | 311.4946 | 3.2954 |  | 0.017537 | 0.017537 | 258.183 | 2.2639 | 258.183 | 2.2639 |  | 0.017468 | 0.017468 | 257.1557 | 2.2459 | 257.1557 | 2.2459
3-4 | 115 | 150 |  | 1 | 4129.3027 | 0.020628 | 170.361 | 1.7571 | 481.8556 | 5.0525 |  | 0.017007 | 0.017007 | 140.4545 | 1.1944 | 398.6374 | 3.4583 |  | 0.016937 | 0.016937 | 139.8782 | 1.1846 | 397.0338 | 3.4305
4-5 | 173 | 150 |  | 1 | 6211.9075 | 0.020151 | 250.3522 | 2.5224 | 732.2079 | 7.575 |  | 0.01653 | 0.01653 | 205.3624 | 1.6973 | 603.9998 | 5.1556 |  | 0.01646 | 0.01646 | 204.4955 | 1.683 | 601.5293 | 5.1135
5-6 | 158 | 150 |  | 1 | 5673.3028 | 0.019602 | 222.421 | 2.18 | 954.6289 | 9.755 |  | 0.015981 | 0.015981 | 181.332 | 1.4489 | 785.3318 | 6.6045 |  | 0.015911 | 0.015911 | 180.5402 | 1.4363 | 782.0695 | 6.5498
6-7 | 110 | 150 | one-loop | 1 | 3949.7678 | 0.017187 | 135.7727 | 1.1668 | 1090.4016 | 10.9217 |  | 0.013566 | 0.013566 | 107.1665 | 0.72692 | 892.4983 | 7.3314 |  | 0.013496 | 0.013496 | 106.6152 | 0.71946 | 888.6848 | 7.2693
7-8 | 128 | 150 |  | 1 | 4596.0934 | 0.016793 | 154.3643 | 1.2961 | 1244.7659 | 12.2179 |  | 0.013172 | 0.013172 | 121.077 | 0.7974 | 1013.5753 | 8.1288 |  | 0.013102 | 0.013102 | 120.4356 | 0.78897 | 1009.1203 | 8.0583
8-9 | 135 | 150 |  | 1 | 4847.4423 | -0.0046339 | 44.9253 | -0.10409 | 1289.6912 | 12.1138 |  | -0.0082552 | -0.0082552 | 80.0329 | -0.33034 | 1093.6083 | 7.7985 |  | -0.008325 | -0.008325 | 80.7095 | -0.33595 | 1089.8298 | 7.7223
9-10 | 155 | 150 |  | 1 | 5565.5819 | -0.0051145 | 56.9307 | -0.14559 | 1346.6219 | 11.9682 |  | -0.0087358 | -0.0087358 | 97.2395 | -0.42473 | 1190.8478 | 7.3738 |  | -0.0088056 | -0.0088056 | 98.0163 | -0.43154 | 1187.8461 | 7.2908
10-11 | 140 | 150 |  | 1 | 5026.9772 | -0.020603 | 207.1461 | -2.134 | 1553.768 | 9.8342 |  | -0.024225 | -0.024225 | 243.554 | -2.95 | 1434.4019 | 4.4238 |  | -0.024294 | -0.024294 | 244.2556 | -2.967 | 1432.1017 | 4.3237
11-2 | 195 | 150 |  | 1 | 7001.8611 | -0.021159 | 296.2998 | -3.1347 | 1850.0677 | 6.6996 | -0.0036213 | -0.02478 | -0.02478 | 347.0109 | -4.2994 | 1781.4127 | 0.12431 | -6.9781e-05 | -0.02485 | -0.02485 | 347.9881 | -4.3237 | 1780.0897 | 4.6159e-05 | -2.5931e-08
[10 empty] | failure | [6 empty] | failure | [6 empty] | failure
Note on R13: If this value is close to 0, we can finish the iteration. If we're under 1 cm (0,01), it is OK.

## pressure flow loss
MAXIMUM CONSUMPTION
Branches | Lenght (m) | Diameter (mm) | Q (m3/s) | Q (l/s) | water velocity (m/s) | local loss (hL) C*Q*abs(Q) (m) | specific pressure flow loss ‰
1-2 | 90 | 200 | 0.035268 | 35.2677 | 1.1226 | 0.95385 | 10.5984
2-3 | 205 | 150 | 0.016308 | 16.3075 | 0.92282 | 1.9575 | 9.5489
3-4 | 115 | 150 | 0.015289 | 15.2893 | 0.8652 | 0.96527 | 8.3937
4-5 | 173 | 150 | 0.014373 | 14.3728 | 0.81334 | 1.2832 | 7.4176
5-6 | 158 | 150 | 0.01332 | 13.3196 | 0.75373 | 1.0065 | 6.3703
6-7 | 110 | 150 | 0.0086828 | 8.6828 | 0.49135 | 0.29778 | 2.7071
7-8 | 128 | 150 | 0.0079255 | 7.9255 | 0.44849 | 0.28869 | 2.2554
8-9 | 135 | 150 | -0.014473 | -14.4734 | -0.81903 | -1.0154 | -7.5218
9-10 | 155 | 150 | -0.015396 | -15.3962 | -0.87125 | -1.3193 | -8.5115
10-11 | 140 | 150 | -0.016335 | -16.3349 | -0.92437 | -1.3414 | -9.5811
11-2 | 195 | 150 | -0.017401 | -17.4009 | -0.98469 | -2.1201 | -10.8724
MINIMUM CONSUMPTION
Branches | Lenght (m) | Diameter (mm) | Q (m3/s) | Q (l/s) | water velocity (m/s) | local loss (hL) C*Q*abs(Q) (m) | specific pressure flow loss ‰
1-2 | 90 | 200 | 0.022233 | 22.2325 | 0.70768 | 0.37906 | 4.2118
2-3 | 205 | 150 | 0.010191 | 10.1914 | 0.57672 | 0.76454 | 3.7295
3-4 | 115 | 150 | 0.010064 | 10.0641 | 0.56951 | 0.41825 | 3.6369
4-5 | 173 | 150 | 0.0099496 | 9.9496 | 0.56303 | 0.61494 | 3.5546
5-6 | 158 | 150 | 0.0098179 | 9.8179 | 0.55558 | 0.54686 | 3.4611
6-7 | 110 | 150 | 0.0092383 | 9.2383 | 0.52278 | 0.3371 | 3.0645
7-8 | 128 | 150 | 0.0091437 | 9.1437 | 0.51743 | 0.38426 | 3.0021
8-9 | 135 | 150 | -0.01148 | -11.4803 | -0.64965 | -0.63888 | -4.7324
9-10 | 155 | 150 | -0.011596 | -11.5956 | -0.65618 | -0.74834 | -4.828
10-11 | 140 | 150 | -0.011713 | -11.713 | -0.66282 | -0.68967 | -4.9262
11-2 | 195 | 150 | -0.011846 | -11.8462 | -0.67036 | -0.98259 | -5.0389
AVERAGE CONSUMPTION
Branches | Lenght (m) | Diameter (mm) | Q (m3/s) | Q (l/s) | water velocity (m/s) | local loss (hL) C*Q*abs(Q) (m) | specific pressure flow loss ‰
1-2 | 90 | 200 | 0.043129 | 43.1294 | 1.3729 | 1.4265 | 15.8501
2-3 | 205 | 150 | 0.017468 | 17.4676 | 0.98846 | 2.2459 | 10.9558
3-4 | 115 | 150 | 0.016937 | 16.9373 | 0.95845 | 1.1846 | 10.3007
4-5 | 173 | 150 | 0.01646 | 16.46 | 0.93144 | 1.683 | 9.7283
5-6 | 158 | 150 | 0.015911 | 15.9114 | 0.9004 | 1.4363 | 9.0906
6-7 | 110 | 150 | 0.013496 | 13.4964 | 0.76374 | 0.71946 | 6.5405
7-8 | 128 | 150 | 0.013102 | 13.102 | 0.74142 | 0.78897 | 6.1638
8-9 | 135 | 150 | -0.008325 | -8.325 | -0.4711 | -0.33595 | -2.4885
9-10 | 155 | 150 | -0.0088056 | -8.8056 | -0.49829 | -0.43154 | -2.7842
10-11 | 140 | 150 | -0.024294 | -24.2945 | -1.3748 | -2.967 | -21.1931
11-2 | 195 | 150 | -0.02485 | -24.8497 | -1.4062 | -4.3237 | -22.1728
Note on D2: data from previous page, the numbers of the last iteration
Note on H2: specific pressure loss should be <10, here 10,6 is acceptable, if it is >15, change the diameter
Note on H32: high pressure loss at average consumption can be ok, because of the fire fighting water

## node pressure
MAXIMUM CONSUMPTION
Node A |  | Branch |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above see) |  | (hL) C*Q*abs(Q) |  | H (m above see) | (m above see) | h (m) | H demand (m)
1 | 40 | 1-2 | 0.95385 | 2 | 39.0461 | 4.49 | 34.5561 | 25 | OK
2 | 39.0461 | 2-3 | 1.9575 | 3 | 37.0886 | 5.26 | 31.8286 | 25 | OK
3 | 37.0886 | 3-4 | 0.96527 | 4 | 36.1233 | 3.49 | 32.6333 | 25 | OK
4 | 36.1233 | 4-5 | 1.2832 | 5 | 34.8401 | 4 | 30.8401 | 25 | OK
5 | 34.8401 | 5-6 | 1.0065 | 6 | 33.8336 | 4.71 | 29.1236 | 25 | OK
6 | 33.8336 | 6-7 | 0.29778 | 7 | 33.5358 | 4.08 | 29.4558 | 25 | OK
7 | 33.5358 | 7-8 | 0.28869 | 8 | 33.2471 | 4.97 | 28.2771 | 25 | OK
8 | 33.2471 | 8-9 | -1.0154 | 9 | 34.2626 | 5.7 | 28.5626 | 25 | OK
9 | 34.2626 | 9-10 | -1.3193 | 10 | 35.5819 | 6.06 | 29.5219 | 25 | OK
10 | 35.5819 | 10-11 | -1.3414 | 11 | 36.9232 | 6 | 30.9232 | 25 | OK
11 | 36.9232 | 11-2 | -2.1201 | 2 | 39.0433 | 4.79 | 34.2533 | 25 | OK
0.0028333
MINIMUM CONSUMPTION
Node A |  | Branch |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above see) |  | (hL) C*Q*abs(Q) |  | H (m above see) | (m above see) | h (m) | H demand (m)
1 | 40 | 1-2 | 0.37906 | 2 | 39.6209 | 4.49 | 35.1309 | 25 | OK
2 | 39.6209 | 2-3 | 0.76454 | 3 | 38.8564 | 5.26 | 33.5964 | 25 | OK
3 | 38.8564 | 3-4 | 0.41825 | 4 | 38.4382 | 3.49 | 34.9482 | 25 | OK
4 | 38.4382 | 4-5 | 0.61494 | 5 | 37.8232 | 4 | 33.8232 | 25 | OK
5 | 37.8232 | 5-6 | 0.54686 | 6 | 37.2763 | 4.71 | 32.5663 | 25 | OK
6 | 37.2763 | 6-7 | 0.3371 | 7 | 36.9392 | 4.08 | 32.8592 | 25 | OK
7 | 36.9392 | 7-8 | 0.38426 | 8 | 36.555 | 4.97 | 31.585 | 25 | OK
8 | 36.555 | 8-9 | -0.63888 | 9 | 37.1939 | 5.7 | 31.4939 | 25 | OK
9 | 37.1939 | 9-10 | -0.74834 | 10 | 37.9422 | 6.06 | 31.8822 | 25 | OK
10 | 37.9422 | 10-11 | -0.68967 | 11 | 38.6319 | 6 | 32.6319 | 25 | OK
11 | 38.6319 | 11-2 | -0.98259 | 2 | 39.6145 | 4.79 | 34.8245 | 25 | OK
0.0064893
AVERAGE CONSUMPTION
Node A |  | Branch |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above see) |  | (hL) C*Q*abs(Q) |  | H (m above see) | (m above see) | h (m) | H demand (m)
1 | 40 | 1-2 | 1.4265 | 2 | 38.5735 | 4.49 | 34.0835 | 25 | OK
2 | 38.5735 | 2-3 | 2.2459 | 3 | 36.3275 | 5.26 | 31.0675 | 25 | OK
3 | 36.3275 | 3-4 | 1.1846 | 4 | 35.143 | 3.49 | 31.653 | 25 | OK
4 | 35.143 | 4-5 | 1.683 | 5 | 33.46 | 4 | 29.46 | 25 | OK
5 | 33.46 | 5-6 | 1.4363 | 6 | 32.0237 | 4.71 | 27.3137 | 25 | OK
6 | 32.0237 | 6-7 | 0.71946 | 7 | 31.3042 | 4.08 | 27.2242 | 25 | OK
7 | 31.3042 | 7-8 | 0.78897 | 8 | 30.5152 | 4.97 | 25.5452 | 25 | OK
8 | 30.5152 | 8-9 | -0.33595 | 9 | 30.8512 | 5.7 | 25.1512 | 25 | OK
9 | 30.8512 | 9-10 | -0.43154 | 10 | 31.2827 | 6.06 | 25.2227 | 25 | OK
10 | 31.2827 | 10-11 | -2.967 | 11 | 34.2498 | 6 | 28.2498 | 25 | OK
11 | 34.2498 | 11-2 | -4.3237 | 2 | 38.5734 | 4.79 | 33.7834 | 25 | OK
4.6159e-05
Note on H2: value should be 25<h<60
Note on D3: data from previos page, local loss
Note on G3: Data from the map, according to the contour lines
Note on B4: pressure of the pump, choose as you like to satisfy the pressure (max 60)
Note on F15: this value should be 0 or close to 0, because it's the same node (2)
Note on D20: data from previos page, local loss
Note on J36: At average consumption pressure might be not satisfied, but check the node where the fire fighting water need is on
Note on D37: data from previos page, local loss

## pressure profile
MAXIMUM CONSUMPTION
Node A |  | Branch |  |  |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above sea) |  | Length (m) | ΣLength (m) | (hL) C*Q*abs(Q) |  | H (m above sea) | (m above sea) | h (m) | H demand (m)
1 | 40 | 1-2 | 90 | 90 | 0.95385 | 2 | 39.0461 | 4.49 | 34.5561 | 25 | OK
2 | 39.0461 | 2-3 | 205 | 295 | 1.9575 | 3 | 37.0886 | 5.26 | 31.8286 | 25 | OK
3 | 37.0886 | 3-4 | 115 | 410 | 0.96527 | 4 | 36.1233 | 3.49 | 32.6333 | 25 | OK
4 | 36.1233 | 4-5 | 173 | 583 | 1.2832 | 5 | 34.8401 | 4 | 30.8401 | 25 | OK
5 | 34.8401 | 5-6 | 158 | 741 | 1.0065 | 6 | 33.8336 | 4.71 | 29.1236 | 25 | OK
6 | 33.8336 | 6-7 | 110 | 851 | 0.29778 | 7 | 33.5358 | 4.08 | 29.4558 | 25 | OK
7 | 33.5358 | 7-8 | 128 | 979 | 0.28869 | 8 | 33.2471 | 4.97 | 28.2771 | 25 | OK
8 | 33.2471 | 8-9 | 135 | 1114 | -1.0154 | 9 | 34.2626 | 5.7 | 28.5626 | 25 | OK
9 | 34.2626 | 9-10 | 155 | 1269 | -1.3193 | 10 | 35.5819 | 6.06 | 29.5219 | 25 | OK
10 | 35.5819 | 10-11 | 140 | 1409 | -1.3414 | 11 | 36.9232 | 6 | 30.9232 | 25 | OK
11 | 36.9232 | 11-2 | 195 | 1604 | -2.1201 | 2 | 39.0433 | 4.79 | 34.2533 | 25 | OK
0.0028333
MINIMUM CONSUMPTION
Node A |  | Branch |  |  |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above sea) |  | Length (m) | ΣLength (m) | (hL) C*Q*abs(Q) |  | H (m above sea) | (m above sea) | h (m) | H demand (m)
1 | 40 | 1-2 | 90 | 90 | 0.37906 | 2 | 39.6209 | 4.49 | 35.1309 | 25 | OK
2 | 39.6209 | 2-3 | 205 | 295 | 0.76454 | 3 | 38.8564 | 5.26 | 33.5964 | 25 | OK
3 | 38.8564 | 3-4 | 115 | 410 | 0.41825 | 4 | 38.4382 | 3.49 | 34.9482 | 25 | OK
4 | 38.4382 | 4-5 | 173 | 583 | 0.61494 | 5 | 37.8232 | 4 | 33.8232 | 25 | OK
5 | 37.8232 | 5-6 | 158 | 741 | 0.54686 | 6 | 37.2763 | 4.71 | 32.5663 | 25 | OK
6 | 37.2763 | 6-7 | 110 | 851 | 0.3371 | 7 | 36.9392 | 4.08 | 32.8592 | 25 | OK
7 | 36.9392 | 7-8 | 128 | 979 | 0.38426 | 8 | 36.555 | 4.97 | 31.585 | 25 | OK
8 | 36.555 | 8-9 | 135 | 1114 | -0.63888 | 9 | 37.1939 | 5.7 | 31.4939 | 25 | OK
9 | 37.1939 | 9-10 | 155 | 1269 | -0.74834 | 10 | 37.9422 | 6.06 | 31.8822 | 25 | OK
10 | 37.9422 | 10-11 | 140 | 1409 | -0.68967 | 11 | 38.6319 | 6 | 32.6319 | 25 | OK
11 | 38.6319 | 11-2 | 195 | 1604 | -0.98259 | 2 | 39.6145 | 4.79 | 34.8245 | 25 | OK
0.0064893
AVERAGE CONSUMPTION
Node A |  | Branch |  |  |  | Node B |  | Ground level | above ground | demand | Pressure
| H (m above sea) |  | Length (m) | ΣLength (m) | (hL) C*Q*abs(Q) |  | H (m above sea) | (m above sea) | h (m) | H demand (m)
1 | 40 | 1-2 | 90 | 90 | 1.4265 | 2 | 38.5735 | 4.49 | 34.0835 | 25 | OK
2 | 38.5735 | 2-3 | 205 | 295 | 2.2459 | 3 | 36.3275 | 5.26 | 31.0675 | 25 | OK
3 | 36.3275 | 3-4 | 115 | 410 | 1.1846 | 4 | 35.143 | 3.49 | 31.653 | 25 | OK
4 | 35.143 | 4-5 | 173 | 583 | 1.683 | 5 | 33.46 | 4 | 29.46 | 25 | OK
5 | 33.46 | 5-6 | 158 | 741 | 1.4363 | 6 | 32.0237 | 4.71 | 27.3137 | 25 | OK
6 | 32.0237 | 6-7 | 110 | 851 | 0.71946 | 7 | 31.3042 | 4.08 | 27.2242 | 25 | OK
7 | 31.3042 | 7-8 | 128 | 979 | 0.78897 | 8 | 30.5152 | 4.97 | 25.5452 | 25 | OK
8 | 30.5152 | 8-9 | 135 | 1114 | -0.33595 | 9 | 30.8512 | 5.7 | 25.1512 | 25 | OK
9 | 30.8512 | 9-10 | 155 | 1269 | -0.43154 | 10 | 31.2827 | 6.06 | 25.2227 | 25 | OK
10 | 31.2827 | 10-11 | 140 | 1409 | -2.967 | 11 | 34.2498 | 6 | 28.2498 | 25 | OK
11 | 34.2498 | 11-2 | 195 | 1604 | -4.3237 | 2 | 38.5734 | 4.79 | 33.7834 | 25 | OK
4.6159e-05
Note on D3: it is the same table than before, D and E columns are added. Length comes from table 'cons. of nodes'