## (1) waterdemand
Determination of designing water demand
(Example)
The calculation of peak water demand is important for the designing. This value is the base of dimension.
Domestic water demand
Count of Connections (piece) | dweller density (person/binding-in) | people of designing area (head) | specific water demand (l/person/day) | average water demand (m3/day) | seasonal ratio b(-) | peak water demand (m3/day) | loss coefficient | designing peak water demand (m3/day)
379 | 3,4 | 1288,6 | 80 | 103.088 | 1.8 | 185.5584 | 1.1 | 204.1142
Count of Connection: We have got some blocks in our designing area, the block is a border of grounds/building sites. The buildings are on these grounds. Every building has a water connection or binding in. The ground' s distance is 15-20 meter betwen themselves. The connection or binding-in joins on the one hand to the ground, on the other hand to the water distribution pipe. The distance of connection depends on the type of settlement. This distance between two connections is larger in a village than in a city. So we have to determine the count of connection.
Dweller density: shows us the number people who joins to the binding-in. For examle so many people live in a flat in average.
Number of people/capitation of designing: This number is calculated from dweller density, and from count of connections (multiply)
Specific water demand is a feature value of the consumption on the actually area. This value depends on the habit of dweller. This value is higher in a rich setllemant, than in a poor one.
Average water demand: This value applies to actually designing area. This value is yearly average water demand of an area.
Seasonal ratio/seasonal variation coefficient shows us the difference between the daily average and the daily peak water demand. Because we have higher water demand on summer, than all-year.
Peak water demand: is highest water demand of people in a year. We can calculate this value from average water demand, and from seasonal ratio. (multiply)
Loss coefficient: Every system has loss so has the water supply system some water loss too. This loss is 10-30 percent in the Hungarian water system So we have to put this loss to the peak water demand. This loss comes from break of pipe, from leak, from cleaning of system, desinfection of the system. This value is pertain of system.
Designing peak water demand: is increased value of peak water demand with the loss.
Public institutions water demand:
We have a public institution on our planning area. We have to choose a block on our planning area, whereon we say that is a public institution. The public institution block has just one connection. We haven't got to add this blocks connection to the dweller connection. We assume there is a grammar school. So There are some workers and lot of students. The student and the teacher have got different water demand. In this part of task, we haven't got to define the people number, because it is available. The calculating of water dimand is like the dweller demand.
Profession of people | Number of people | specific water demand (l/person/day) | average water demand (m3/day) | seasonal ratio | peak water demand (m3/day) | loss coefficient | designing peak water demand (m3/day)
worker | 60 | 120 | 7.2 | 1.8 | 12.96 | 1.1 | 14.256
student | 800 | 120 | 96 | 1.8 | 172.8 | 1.1 | 190.08
The industrial water demand:
We have an industrial area in our planning area. We have to choose a block on our planning area, whereon we say that is a industy. The industry block has just one connection. We haven't got to add this blocks connection to the dweller connection. The industry has two water demands oneside technological demand otherside the social water demand. The technological water is used to product fabricating. We calculate the social water demand as the dweller. We don' t have to define the worker number because it is available. We assume in this task that the technological water demand doesn' t vary in the year. It is fix. There are some branches of industry, where the seasonal ratio differs from 1,00 for example the cannery. The seasonal ratio of technological water demand is 1,00 in this task.
Technological water demand (m3/day) | Loss coefficient | designing peak water demand (m3/day)
1400 | 1.1 | 1540
Number of People | specific water demand (l/person/day) | average water demand (m3/day) | seasonal ratio | peak water demand (m3/day) | loss coefficient | designing peak water demand (m3/day)
250 | 130 | 32.5 | 1.8 | 58.5 | 1.1 | 64.35
The designing water demand
The full designing water demand of area contains the sum of following water demand: - dweller demand - the public institute demand - idustrial water demand
The full water demand: |  | 1998.5442 | m3/d

## (2) wastewaterdemand
Determinate of waste water
We are going to design a gravitational separeted waste water system on our designing area. The meaning of the separeted system is that the waste water and the storm water flow in the different pipes. We calculate the waste water quantity from the water consumtion. The waste water pipe is dimensioned for maximum waste water quantity. The maximum waste water quantity is calculated with following value: - the peak water demand without loss - waste-water fraction - hourly-peak ratio
Derivation of waste water | maximum water consumption (m3/day) | Waste water fraction / sewage ratio | Maximum waste water quantity (m3/day) | hourly-peak ratio | hourly maximum waste water quantity (m3/hour)
dweller | 204.1142 | 0.9 | 183.7028 | 0.056 | 10.2874
public institution | 204.336 | 0.9 | 183.9024 | 0.056 | 10.2985
technological water | 1540 | 0.9 | 1386 | 0.056 | 77.616
social water | 64.35 | 0.9 | 57.915 | 0.056 | 3.2432
The peak water demand: We use this value and not the designing water, because the loss of water won' t waste water.
Waste-water fraction/sewage ratio: This value shows us how much proportion of water will waste water. It depends on the applications mode of water. For example in a village, where the water is used for watering to this value is lower than in a city center.
Hourly peak ratio/Peak flow coefficient show us how many proportion of waste water flows in the peak hour in the drainage. This value is varied by the peoples habbit. For example this value in a small village is 1/10 in a big city is 1/22.
Design of the pipes
First, we can calculate the loads for each design point :
Point number | Catchment | Catchment areas | Waste water load due to : |  |  |  | Total design load
|  |  | Inhabitants | Public institution | Communal demand | Technological demand
|  | [m2] | [m3/h] | [m3/h] | [m3/h] | [m3/h] | [m3/h]
0 | S1 + S2 + S3 + S4 | 393100 | 10.2874 | 10.2985 | 3.2432 | 77.616 | 101.4451
1 | S1 | 94075 | 48.8477 |  | 3.2432 | 77.616 | 129.707
2 | S2 | 94075 | 48.8477 |  |  |  | 48.8477
3 | S3 | 82650 | 42.9154 | 10.2985 |  |  | 53.2139
4 | S4 | 122300 | 63.5034 |  | 3.2432 | 77.616 | 144.3626
| TOTAL AREA OF THE ZONE : | 393100
Then, we can define at what depth in the soil we have to bury the pipes of the network :
Pipe number | Length of the pipes | Depth of the inlet point of the pipe | Depth of the outlet point of the pipe | Slope
| [m] | [m] | [m] | [‰]
0 | 270 | 6.65 | 8 | 5
1 | 155 | 5.875 | 6.65 | 5
2 | 200 | 4.875 | 5.875 | 5
3 | 110 | 4.325 | 4.875 | 5
4 | 180 | 3.425 | 4.325 | 5
Finally, we can find the diameter of the pipes :
Pipe number | Slope | Roughness of the pipe | Diameter of the pipes d | vtot | Qtot | Qdesign | Qdesign/Qtot
| [‰] | [mm] | [m] | [m/s] | [L/s] | [L/s]
0 | 1 | 0.5 | 0.25 | 0.43962 | 21.5798 | 28.1792 | 1.3058
1 | 1 | 0.5 | 0.2 | 0.37943 | 11.9202 | 36.0297 | 3.0226
2 | 1 | 0.5 | 0.2 | 0.37943 | 11.9202 | 13.5688 | 1.1383
3 | 1 | 0.5 | 0.2 | 0.37943 | 11.9202 | 14.7816 | 1.24
4 | 1 | 0.5 | 0.2 | 0.37943 | 11.9202 | 40.1007 | 3.3641
vdesign/vtot and the ratio h/d from Qdesign/Qtot :
Pipe number | Qdesign/Qtot | vdesign/vtot | h/d | Diameter of the pipes d | h | vtot | vreal
| [%] | [%] | [%] | [m] | [m] | [m/s] | [m/s]
0 | 130.5816 | 98 | 67 | 0.25 | 0.1675 | 0.43962 | 0.43083
1 | 302.2576 | 80 | 47 | 0.2 | 0.094 | 0.37943 | 0.30355
2 | 113.8304 | 83 | 50 | 0.2 | 0.1 | 0.37943 | 0.31493
3 | 124.005 | 69 | 33 | 0.2 | 0.066 | 0.37943 | 0.26181
4 | 336.4097 | 79 | 45 | 0.2 | 0.09 | 0.37943 | 0.29975